Comprehensive Experiment Report

( School Year 20   -- 20   )

Topic：     Substation Simulation Comprehensive Experiment

Department：

Class：

Student ID：

Student Name：

Faculty adviser：

Scores：

Date：

- I.Learning Objectives and Requirements of Comprehensive experiment

- In the experiment,students should understand the actual requirements of the power system , and master the skills which operating personnel should obtain through practical actions and simulation exercises.Then it can enhance perceptual knowledge of grid operation , equipment maintenance and other practical knowledge and improve their abilities of integrating theory with practice and competitiveness in the work.

- Basic requirements

2.1 Students are required to take the training class before use the computer yourself,and answer the questions.

2.2 Students are required to do simulation operation in the class,and finish the comprehensive experiment report.

2.3 Students are required to take the exam on the machine and defence examination.

- II.Main body of experiment

- Power grid/Transformer substation simulation System and Monitoring of the Normal operation

1.1  Primary equipment（From main electrical connection）

| Name of Equipment | Graphic Symbol | Its color and Symbol when closing | Its color and Symbol when opening | Effect |
| --- | --- | --- | --- | --- |
| Circuit breaker |  |  |  |  |
| disconnector |  |  |  |  |
| Grounding switch |  |  |  |  |
| Main transformer |  |  |  |  |
| CT （Current transformer） |  |  |  |  |
| PT （Potential transformer） |  |  |  |  |
| Lightning arrester |  |  |  |  |
| Capacitor |  |  |  |  |
| Arc extinguishing coil |  |  |  |  |

- 1.2 Connection type of main electrical connection and Operation mode

- 1.2.1 Fill in a form

| - Voltage level | - Connection type | - Interval Equipment | - Normal operation mode |
| --- | --- | --- | --- |
| - 220kV | - double-bus type connection | - 251 Line 1 | - Operating on 220kV Bus 1 |
|  |  | - 252 Line 2 |  |
|  |  | - 253 Line 3 |  |
|  |  | - 254 Line 4 |  |
|  |  | - 255 Line 5 |  |
|  |  | - 212 bus-tie |  |
| - 110kV |  |  |  |
| - 35kV | - Single bus connection |  |  |

| Main transformer | Voltage level | Normal operation mode | Neutral point operation mode |
| --- | --- | --- | --- |
| Main transformer 1 |  |  | Neutral grounding |
|  |  |  | Neutral non-grounding |
| Main transformer 2 |  |  |  |

1.2.2 Summary

（1）What are regularities with the numbers of Circuit breakers and Disconnectors？

（2）What are regularities between numbers of Circuit breakers and operation mode ？

- 1.3 Operation and monitoring of Bay Equipments 251(Do what exactly you are told in the following)

1.3.1 Equipment states in Normal operation mode

（1）Go to the Bay Equipments251 monitoring detail drawing in monitoring system.Check and record Monitoring contents in monitoring computer.

| remote communication information |  | remote communication information |  |
| --- | --- | --- | --- |
| State of Circuit breaker 251 |  | active power |  |
| State of disconnector 2516 |  | reactive power |  |
| State of disconnector 2511 |  | electric current |  |
| State of disconnector 2512 |  | power factor |  |
| Protection signal lights which are shining |  |  |  |

（2）Go to the Measurement and Control cubicle in Protection room to Check and record State of bay Equipments 251

| Measurement and Control Equipment of 251仿一线(FCK-801) | Effect: Lights which are shining: |
| --- | --- |
| The position of control switch of Circuit breaker 251 |  |
| Signal light of Circuit breaker 251 |  |
| Local-Remote swith of Circuit breaker 251 |  |

（3）Go to the bay Equipments 251 in outdoor to check and record States of Circuit breakers and Disconnectors

| State of Circuit breaker 251 |  | State of disconnector 2511 |  |
| --- | --- | --- | --- |
| State of disconnector 2516 |  | State of disconnector 2512 |  |

（4）Go to the protection room to check and record states of protection cubicle of 251 Line 1

·251 Line 1 protection cubicle I（cubicle NO.40）

| Name of Equipment | States of Protection signal lights on equipment | Functions of Equipment |
| --- | --- | --- |
| Reclosure swith: |  |  |

·251 Line 1 Protection cubicle II（cubicle NO.41）

| Name of Equipment | States of Protection signal lights on equipment | Functions of Equipment |
| --- | --- | --- |
| Reclosure swith: |  |  |

·251 Line 1 Auxiliary Protection cubicle I（cubicle NO.42）

| Name of Equipment | States of Protection signal lights on equipment | Functions of Equipment |
| --- | --- | --- |

1.3.2 Open Circuit breaker 251 in monitoring system，then check and record states in monitoring computer、equipments in outdoor、protection room and Measurement and Control cubicle, and figure out what have changed

(1) Bay Equipments251’s  monitoring detail drawing in monitoring system：

(2)Measurement and Control cubicle in Protection room：

(3) Bay Equipments 251 in outdoor：

(4)Protection cubicle of 251 in the protection room:

·251 Line 1 Protection cubicle I（cubicle NO.40）：

·251 Line 1 Protection cubicle II（cubicle NO.41）:

·251 Line 1 Auxiliary Protection cubicle I（cubicle NO.42）:

1.3.3 Open disconnector 2516 in monitoring system，then check and record states in monitoring computer、equipments in outdoor、protection room and Measurement and Control cubicle, and figure out what have changed.

(1) Bay Equipments251’s  monitoring detail drawing in monitoring system：

(2)Measurement and Control cubicle in Protection room：

(3) Bay Equipments 251 in outdoor：

(4)Protection cubicle of 251 in the protection room:

·251 Line 1 Protection cubicle I（cubicle NO.40）：

·251 Line 1 Protection cubicle II（cubicle NO.41）:

·251 Line 1 Auxiliary Protection cubicle I（cubicle NO.42）:

1.3.4  Open disconnector 2511 in outdoor，then check and record States in monitoring computer、Equipments in outdoor、protection room and Measurement and Control cubicle, and figure out what have changed.

(1)Bay Equipments 251 in outdoor：

(2)Measurement and Control cubicle in Protection room：

(3) Bay Equipments251’s  monitoring detail drawing in monitoring system：

(4)Protection cubicle of 251 in the protection room:

·251 Line 1 Protection cubicle I（cubicle NO.40）：

·251 Line 1 Protection cubicle II（cubicle NO.41）:

·251 Line 1 Auxiliary Protection cubicle I（cubicle NO.42）:

1.3.5 Close Grounding switch 2517 in outdoor,then check and record States in monitoring computer,Equipments in outdoor,protection room and Measurement and Control cubicle,and figure out what have changed.

(1) Bay Equipments 251 in outdoor：

(2)Measurement and Control cubicle in Protection room：

(3) Bay Equipments251 monitoring detail drawing in monitoring system：

(4)Protection cubicle of 251 in the protection room:

·251 Line 1 Protection cubicle I（cubicle NO.40）：

·251 Line 1 Protection cubicle II（cubicle NO.41）:

·251 Line 1 Auxiliary Protection cubicle I（cubicle NO.42）:

1.3.6 Close Circuit breaker 251 in Measurement and Control cubicle ,then check and record States in monitoring computer,Equipments in outdoor,protection room and Measurement and Control cubicle,and figure out what have changed.

(1)Measurement and Control cubicle in Protection room：

(2) Bay Equipments251 monitoring detail drawing in monitoring system：

(3) Bay Equipments 251 in outdoor：

(4)Protection cubicle of 251 in the protection room:

·251 Line 1 Protection cubicle I（cubicle NO.40）：

·251 Line 1 Protection cubicle II（cubicle NO.41）:

·251 Line 1 Auxiliary Protection cubicle I（cubicle NO.42）:

1.3.7  Question answering

（1）How many protection series is 251 Line 1 equipped？Reclosure operation mode？

（2）Summary when lights of equipments are on or off

| CSC103B“Charging”light |  |
| --- | --- |
| RSC931“Charging”light |  |
| JFZ-12F“A phase open”light |  |
| JFZ-12F“A phase close”light |  |
| JFZ-12F“I Bus operating”light |  |

1.4 Protection series of 151 tie line

（1）check states of Protection and operation mode

| Name and NO. of Protection cubicle | Name of Equipment | States of Protection signal lights on equipment when run normally | Functions of Equipment |
| --- | --- | --- | --- |

（2）How many protection series is 151 tie line  equipped？

2.Inspection of electrical equipments

2.1 Inspection of Main transformer 1

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| Front: bushing’s porcelain insulation of 220kV A phase |  |  | Back: bushing’s porcelain insulation of 110kV A phase |  |  |
| Front: bushing’s oil level of 220kV A phase |  |  | Back: bushing’s oil level of 110kV A phase |  |  |
| Front: bushing’s lead wire joint of 220kV A phase |  |  | Back: bushing’s lead wire joint of 110kV A phase |  |  |
| Front: bushing’s porcelain insulation of 220kV B phase |  |  | Back: bushing’s porcelain insulation of 110kV B phase |  |  |
| Front: bushing’s oil level of 220kV B phase |  |  | Back: bushing’s oil level of 110kV B phase |  |  |
| Front: bushing’s lead wire joint of 220kV B phase |  |  | Back: bushing’s lead wire joint of 110kV B phase |  |  |
| Front: bushing’s porcelain insulation of 220kV C phase |  |  | Back: bushing’s porcelain insulation of 110kV C phase |  |  |
| Front: bushing’s oil level of 220kV C phase |  |  | Back: bushing’s oil level of 110kV C phase |  |  |
| Front: bushing’s lead wire joint of 220kV C phase |  |  | Back: bushing’s lead wire joint of 110kV C phase |  |  |
| Front: bushing’s porcelain insulation of 220kV neutral point |  |  | Back: bushing’s porcelain insulation of 35kV A phase |  |  |
| Front: bushing’s oil level of 220kV neutral point |  |  | Back: bushing’s lead wire joint of 35kV A phase |  |  |
| Front: bushing’s lead wire joint of 220kV neutral point |  |  | Back: bushing’s porcelain insulation of 35kV B phase |  |  |
| Front: Fan1 |  |  | Back: bushing’s lead wire joint of 35kV B phase |  |  |
| Front: Fan2 |  |  | Back: bushing’s porcelain insulation of 35kV C phase |  |  |
| Front: Fan3 |  |  | Back: bushing’s lead wire joint of 35kV C phase |  |  |
| Front: Fan4 |  |  | Left: oil level of on-load voltage regulating device |  |  |
| Front: Fan5 |  |  | Left: tap position of on-load voltage regulating mechanical box |  |  |
| Front: Fan6 |  |  | Left:online oil filter |  |  |
| Front: Fan7 |  |  | Left: bushing’s porcelain insulation of 110kV neutral point |  |  |
| Front: Fan8 |  |  | Left: bushing’s oil level of 110kV neutral point bushing |  |  |
| Front: Fan9 |  |  | Left: bushing’s lead wire joint of 110kV neutral point |  |  |
| Front: Fan10 |  |  | Left: earthing conductor of switchyard structure |  |  |
| Front: oil level of gas relay |  |  | Right: oil level of oil conservator |  |  |
| Front: oil color of gas relay |  |  | Right:winding thermometer |  |  |
| Front: Oil-flow relay1 |  |  | Right:upper oil thermometer |  |  |
| Front: Oil-flow relay2 |  |  | Right:lower oil thermometer |  |  |
| Front: Oil-flow relay3 |  |  | Right: earthing conductor of switchyard structure |  |  |
| Front: Oil-flow relay4 |  |  |  |  |  |
| Front: Oil-flow relay5 |  |  |  |  |  |
| Front: Oil trace on the ground |  |  |  |  |  |

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| 220kV lightning arrester: bushing’s lead wire joint of A phase |  |  | 220kV lightning arrester: leakage current of B phase |  |  |
| 220kV lightning arrester: bushing’s porcelain insulation of A phase |  |  | 220kV lightning arrester: earthing conductor of B phase |  |  |
| 220kV lightning arrester: leakage current of A phase |  |  | 220kV lightning arrester: bushing’s lead wire joint of C phase |  |  |
| 220kV lightning arrester: earthing conductor of A phase |  |  | 220kV lightning arrester: bushing’s porcelain insulation of C phase |  |  |
| 220kV lightning arrester: lead wire joint of B phase bushing |  |  | 220kV lightning arrester: leakage current of C phase |  |  |
| 220kV lightning arrester: porcelain insulation of B phase bushing |  |  | 220kV lightning arrester: earthing conductor of C phase |  |  |

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| 110kV lightning arrester: earthing conductor 1 |  |  | 110kV lightning arrester: bushing’s porcelain insulation of B phase |  |  |
| 110kV lightning arrester: earthing conductor 2 |  |  | 110kV lightning arrester: leakage current of B phase |  |  |
| 110kV lightning arrester: bushing’s lead wire joint of A phase |  |  | 110kV lightning arrester: bushing’s lead wire joint of C phase |  |  |
| 110kV lightning arrester: bushing’s porcelain insulation of A phase |  |  | 110kV lightning arrester: bushing’s porcelain insulation of C phase |  |  |
| 110kV lightning arrester: leakage current of A phase |  |  | 110kV lightning arrester: leakage current of C phase |  |  |
| 110kV lightning arrester：bushing’s lead wire joint of B phase |  |  |  |  |  |

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| 35kV lightning arrester : bushing’s lead wire joint of A phase |  |  | 35kV lightning arrester: leakage current of B phase |  |  |
| 35kV lightning arrester: bushing’s porcelain insulation of A phase |  |  | 35kV lightning arrester: bushing’s lead wire joint of C phase |  |  |
| 35kV lightning arrester: leakage current of A phase |  |  | 35kV lightning arrester: bushing’s porcelain insulation of C phase |  |  |
| 35kV lightning arrester: bushing’s lead wire joint of B phase |  |  | 35kV lightning arrester: leakage current of C phase |  |  |
| 35kV lightning arrester: bushing’s porcelain insulation of B phase |  |  | 35kV lightning arrester: Earthing conductor |  |  |

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| 220kV neutral point: state of earthing switch |  |  | 110kV neutral point: porcelain insulation 3 of earthing switch |  |  |
| 220kV neutral point: porcelain insulation 1 of earthing switch |  |  | 110kV neutral point: Joint of earthing switch |  |  |
| 220kV neutral point: porcelain insulation 2 of earthing switch |  |  | 110kV neutral point: contact of earthing switch |  |  |
| 220kV neutral point: porcelain insulation 3 of earthing switch |  |  | 110kV neutral point: oil level of CT |  |  |
| 220kV neutral point: joint of earthing switch |  |  | 35kV neutral point: State of earthing switch |  |  |
| 220kV neutral point: contact of earthing switch |  |  | 35kV neutral point: porcelain insulation 1 of earthing switch |  |  |
| 220kV neutral point: oil level of CT |  |  | 35kV neutral point: porcelain insulation 2 of earthing switch |  |  |
| 110kV neutral point: State of earthing switch |  |  | 35kV neutral point: joint1 of switch |  |  |
| 110kV neutral point: porcelain insulation 1 of earthing switch |  |  | 35kV neutral point: joint2 of switch |  |  |
| 110kV neutral point: porcelain insulation 2 of earthing switch |  |  | 35kV neutral point: contact of switch |  |  |

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| arc extinguishing coil: Earthing conductor of lightning arrester |  |  | arc extinguishing coil: joint2 |  |  |
| arc extinguishing coil: porcelain insulation of lightning arrester |  |  | arc extinguishing coil: joint3 |  |  |
| arc extinguishing coil:joint of lightning arrester |  |  | arc extinguishing coil: Silica gel1 |  |  |
| arc extinguishing coil: Oil trace on the ground |  |  | arc extinguishing coil: Silica gel2 |  |  |
| arc extinguishing coil: thermometer |  |  | arc extinguishing coil: oil level of gas relay |  |  |
| arc extinguishing coil: porcelain insulation 1 |  |  | arc extinguishing coil: oil color of gas relay |  |  |
| arc extinguishing coil: porcelain insulation 2 |  |  | arc extinguishing coil: oil level 1 of oil conservator |  |  |
| arc extinguishing coil: porcelain insulation 3 |  |  | arc extinguishing coil: oil leve 2 of oil conservator |  |  |
| arc extinguishing coil: joint1 |  |  | arc extinguishing coil: Draining oil valve |  |  |

2.2  Inspection of Circuit breaker 251

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| open/closed position indicator of A phase |  |  | lead wire joint2 of B phase |  |  |
| porcelain insulation of A phase |  |  | SF6 pressure meter of B phase |  |  |
| lead wire joint1 of A phase |  |  | Energy storage instrument of B phase |  |  |
| lead wire joint2 of A phase |  |  | open/closed position indicator of C phase |  |  |
| SF6 pressure meter of A phase |  |  | porcelain insulation of C phase |  |  |
| Energy storage indicator of A phase |  |  | lead wire joint1 of C phase |  |  |
| open/closed position indicator of B phase |  |  | lead wire joint2 of C phase |  |  |
| porcelain insulation of B phase |  |  | SF6 pressure meter of C phase |  |  |
| lead wire joint1 of B phase |  |  | Energy storage indicator of C phase |  |  |

2.3 Inspection of CT251

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| porcelain insulation of A phase |  |  | oil level of B phase |  |  |
| lead wire joint1 of A phase |  |  | Flange(oil leak) of B phase |  |  |
| lead wire joint2 of A phase |  |  | porcelain insulation of C phase |  |  |
| oil level of A phase |  |  | lead wire joint1 of C phase |  |  |
| Flange(oil leak) of A phase |  |  | lead wire joint2 of C phase |  |  |
| porcelain insulation of B phase |  |  | oil level of C phase |  |  |
| lead wire joint1 of B phase |  |  | Flange(oil leak) of C phase |  |  |
| lead wire joint2 of B phase |  |  |  |  |  |

2.4  Inspection of disconnector 2516

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| state |  |  | lead wire joint2 of B phase |  |  |
| porcelain insulation 1 of A phase |  |  | contact of B phase |  |  |
| porcelain insulation 2 of A phase |  |  | pin of B phase |  |  |
| lead wire joint1 of A phase |  |  | porcelain insulation 1 of C phase |  |  |
| lead wire joint2 of A phase |  |  | porcelain insulation 2 of C phase |  |  |
| contact of A phase |  |  | lead wire joint1 of C phase |  |  |
| pin of A phase |  |  | lead wire joint2 of C phase |  |  |
| porcelain insulation 1 of B phase |  |  | contact of C phase |  |  |
| porcelain insulation 2 of B phase |  |  | pin of C phase |  |  |
| lead wire joint1 of B phase |  |  |  |  |  |

2.5 Inspection of wave trap coil 251,PT,coupling capacitor

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| wave trap coil of 251 A phase : porcelain insulation |  |  | wave trap coil of 251 C phase : lead wire joint1 |  |  |
| wave trap coil of 251 A phase : lead wire joint1 |  |  | wave trap coil of 251 C phase: lead wire joint2 |  |  |
| wave trap coil of 251 A phase : lead wire joint2 |  |  | wave trap coil of 251 C phase: internal foreign body |  |  |
| wave trap coil of 251 A phase : internal foreign body |  |  | Line PT and coupling capacitor of 251 C phase: porcelain insulation |  |  |
| wave trap coil of 251 B phase: porcelain insulation |  |  | Line PT and coupling capacitor of 251 C phase: lead wire joint |  |  |
| wave trap coil of 251 B phase: lead wire joint1 |  |  | Line PT and coupling capacitor of 251 C phase: Flange |  |  |
| wave trap coil of 251 B phase: lead wire joint2 |  |  | Line PT and coupling capacitor of 251 C phase: oil level |  |  |
| wave trap coil of 251 B phase: internal foreign body |  |  | coupling capacitor of 251 A phase : joint |  |  |
| wave trap coil of 251 C phase: porcelain insulation |  |  | coupling capacitor of 251 A phase : porcelain insulation |  |  |

2.6 Inspection of PT and lightning arrester of 220kV Bus I

(1) 219PT of 220kV Bus I

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| porcelain insulation of A phase |  |  | porcelain insulation of C phase |  |  |
| lead wire joint of A phase |  |  | lead wire joint of C phase |  |  |
| oil level of A phase |  |  | oil level of C phase |  |  |
| Flange(oil leak) of A phase |  |  | Flange(oil leak) of C phase |  |  |
| porcelain insulation of B phase |  |  | airtightness of terminal box |  |  |
| lead wire joint of B phase |  |  | Wiring heat |  |  |
| oil level of B phase |  |  | dampness of terminal box |  |  |
| Flange(oil leak) of B phase |  |  |  |  |  |

(2) lightning arrester of 219 PT

| inspection items | current state | Defect(Y/N) | inspection items | current state | Defect(Y/N) |
| --- | --- | --- | --- | --- | --- |
| lead wire joint of A phase |  |  | leakage current of B phase |  |  |
| porcelain insulation A phase |  |  | earthing conductor of B phase |  |  |
| leakage current of A phase |  |  | lead wire joint of C phase |  |  |
| earthing conductor of A phase |  |  | porcelain insulation C phase |  |  |
| lead wire joint of B phase |  |  | leakage current of C phase |  |  |
| porcelain insulation B phase |  |  | earthing conductor of C phase |  |  |

3． Electric switching operation

3.1 Switching operation of isolating equipment in the Normal operation mode

| Equipment which need to be isolated | Circuit breakers which need to be open |
| --- | --- |
| 251 Line 1 |  |
| 151 Tie- line |  |
| 351 Feeder 1 |  |
| 220kV Bus I |  |
| 110kV Bus II |  |
| 35kV Bus I |  |
| Main transformer1 |  |

- 3.2 Cognition of operation states

- The operation states of power system are divided into 4 types: operating ,hot reserve,cold reserve and maintenance.Please figure out the states of corresponding circuit breakers, disconnectores, grounding switches in different operation states.

| - name of equipment | - operating | - hot reserve | - cold reserve | - maintenance |
| --- | --- | --- | --- | --- |
| - 251 Line 1 |  |  |  |  |
| - circuit breaker 251 |  |  |  |  |
| - 220kV BusⅠ |  |  |  |  |
| - main transformer1 |  |  |  |  |

- 3.3 Finish switching operation order which can make circuit breaker 251 that in operating state to maintenance state in the 220kV simulation station,then do it in your simulation system(without the secondary equipment).

**Electric switching operation order

- Transformer substation：220kV  ** Substation     　　　　　NO.

| commander |  |  | operator |  | Time of command | Y M D H M |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Start time of operation： Y M D H M |  |  |  |  | End time of operation： Y M D H M |  |  |
| （ ）Under supervision ( ) Alone （ ）By Maintainers |  |  |  |  |  |  |  |
| Operation task： |  |  |  |  |  |  |  |
| sequence | Operation detail |  |  |  |  |  | Executed√ |
| Remarks： Examiner： |  |  |  |  |  |  |  |
| Operator： Supervisor： Person in charge： |  |  |  |  |  |  |  |

**Electric switching operation order

Transformer substation：220kV  ** Substation     　　　NO.

| commander |  |  | operator |  | Time of command | Y M D H M |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Start time of operation： Y M D H M |  |  |  |  | End time of operation： Y M D H M |  |  |
| （ ）Under supervision ( ) Alone （ ）By Maintainers |  |  |  |  |  |  |  |
| Operation task： |  |  |  |  |  |  |  |
| sequence | Operation detail |  |  |  |  |  | Executed√ |
| Remarks： Examiner： |  |  |  |  |  |  |  |
| Operator： Supervisor： Person in charge： |  |  |  |  |  |  |  |

- 3.4 Finish switching operation order which can make 220 kV bus I that in operating state to maintenance state and make the loads supplied by bus II in the 220kV simulation station,then do it in your simulation system(without the secondary equipment).

**Electric switching operation order

- Transformer substation：220kV  ** Substation     　　　　　NO.

| commander |  |  | operator |  | Time of command | Y M D H M |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Start time of operation： Y M D H M |  |  |  |  | End time of operation： Y M D H M |  |  |
| （ ）Under supervision ( ) Alone （ ）By Maintainers |  |  |  |  |  |  |  |
| Operation task： |  |  |  |  |  |  |  |
| sequence | Operation detail |  |  |  |  |  | Executed√ |
| Remarks： Examiner： |  |  |  |  |  |  |  |
| Operator： Supervisor： Person in charge： |  |  |  |  |  |  |  |

**Electric switching operation order

Transformer substation：220kV  ** Substation     　　　NO.

| commander |  |  | operator |  | Time of command | Y M D H M |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Start time of operation： Y M D H M |  |  |  |  | End time of operation： Y M D H M |  |  |
| （ ）Under supervision ( ) Alone （ ）By Maintainers |  |  |  |  |  |  |  |
| Operation task： |  |  |  |  |  |  |  |
| sequence | Operation detail |  |  |  |  |  | Executed√ |
| Remarks： Examiner： |  |  |  |  |  |  |  |
| Operator： Supervisor： Person in charge： |  |  |  |  |  |  |  |

- 3.5 Finish switching operation order which can make main transformer1 that in operating state to maintenance state in the 220kV simulation station,then do it in your simulation system(without the secondary equipment).

**Electric switching operation order

- Transformer substation：220kV  ** Substation     　　　　　NO.

| commander |  |  | operator |  | Time of command | Y M D H M |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Start time of operation： Y M D H M |  |  |  |  | End time of operation： Y M D H M |  |  |
| （ ）Under supervision ( ) Alone （ ）By Maintainers |  |  |  |  |  |  |  |
| Operation task： |  |  |  |  |  |  |  |
| sequence | Operation detail |  |  |  |  |  | Executed√ |
| Remarks： Examiner： |  |  |  |  |  |  |  |
| Operator： Supervisor： Person in charge： |  |  |  |  |  |  |  |

**Electric switching operation order

Transformer substation：220kV  ** Substation     　　　NO.

| commander |  |  | operator |  | Time of command | Y M D H M |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Start time of operation： Y M D H M |  |  |  |  | End time of operation： Y M D H M |  |  |
| （ ）Under supervision ( ) Alone （ ）By Maintainers |  |  |  |  |  |  |  |
| Operation task： |  |  |  |  |  |  |  |
| sequence | Operation detail |  |  |  |  |  | Executed√ |
| Remarks： Examiner： |  |  |  |  |  |  |  |
| Operator： Supervisor： Person in charge： |  |  |  |  |  |  |  |

- 3.6  Circuit breaker 251 is in operating state in the 220kV simulation station. If operating crew found that the controls of circuit breaker 251 were broken,which could not open, What should operating crew do to get it out of operation?

- 4. Power system fault and its recovery processing

4.1 Basic conception of line protection

（1）Which  CT’s and PT’s measured values do we need for protection device of 仿一线in 220kV simulation station?仿真（location of CT and PT）

（2）If Protection device of 仿一线in 220kV simulation station operates，which Circuit breakers will open？

（3）Point out the protective zone of Protection device of 仿一线in 220kV simulation station.

（4）What is the Reclosing operation mode of 仿一线in 220kV simulation station（single-phase reclosing,three-phase reclosing,Three Phase Auto reclosing）？Then finish the form：

| Line fault conditions | Describe the process of breakers’ action |
| --- | --- |
| A permanent,single-phase ground short circuit |  |
| A permanent, non-single-phase ground short circuit |  |
| A transient,single-phase ground short circuit |  |
| A transient, non-single-phase ground short circuit |  |

4.2 Prediction failure

Protection types and Operation Time of two series of Protection devices of 仿一线 are given as follows.Suppose there is a permanent,single-phase ground short circuit fault at 仿一线 0% from the transformer substation,finish the form.

| RCS-931B |  |  | CSC-103B |  |  |
| --- | --- | --- | --- | --- | --- |
| Protection types | Operation Time | Operated (Y/N) | Protection types | Operation Time | Operated (Y/N) |
| 纵联分相电流差动 Pilot Split Phase current differential protection | 0s |  | 纵联距离 Pilot protection | 0s |  |
| 纵联零序电流差动 Pilot zero sequence current differential protection | 0s |  | 相间距离1段 Phase distance I | 0s |  |
| 相间距离1段 Phase distance I | 0s |  | 相间距离2段 Phase distance II | 1s |  |
| 相间距离2段 Phase distance II | 1s |  | 相间距离3段 Phase distance III | 3s |  |
| 相间距离3段 Phase distance III | 3s |  | 接地距离1段 Ground distance I | 0s |  |
| 接地距离1段 Ground distance I | 0s |  | 接地距离2段 Ground distance II | 9.9s |  |
| 接地距离2段 Ground distance II | 9.9s |  | 接地距离3段 Ground distance III | 9.9s |  |
| 接地距离3段 Ground distance III | 9.9s |  | 零序电流1段 Zero sequence current I | 0s |  |
| 零序电流1段 Zero sequence current I | 0s |  | 零序电流2段 Zero sequence current II | 1s |  |
| 零序电流2段 Zero sequence current II | 1s |  | 零序电流3段 Zero sequence current III | 2s |  |
| 零序电流3段 Zero sequence current III | 2s |  | 重合闸(投单重) Reclosure (single-phase) |  |  |
| 重合闸(投单重) Reclosure (single-phase) |  |  |  |  |  |

4.3 Fault stimulation    Set 251仿一线wave trapper 251 A phase insulator flashover阻波器A相绝缘子闪络。

（1）Fault phenomenon

| Equipment | Phenomenon |
| --- | --- |
| Master-control room： | 1．Fault Sound 2．Circuit breakers which are opening or closing： Bus voltage： 3．Message： 4．251仿一线monitoring detail drawing： |
| Protection room： Screen NO. |  |
| Protection room： Screen NO. |  |
| Protection room： Screen NO. |  |
| Protection room： Measurement and control screen |  |
| Protection room： 220kV line fault recording screen 110kV line fault fault recording screen Main transformer1 fault fault recording screen Main transformer2 fault fault recording screen |  |

（2）How to locate the fault according to the Fault phenomenon above?Why?

（3）After the fault,which equipments should the person on duty check seriously?Then work out the recovery process.

（4）How to isolate the failure equipments?

（5）Which equipments(non-failure) are without power because of the fault?Then work out the recovery process.

4.4 Basic conception of Bus protection

（1）Which CT’s measured values do we need for Bus protection of 220kV Bus I in stimulation station?仿真（location of CT ）

（2）If Bus protection of 220kV Bus I in 220kV stimulation station operates，which Circuit breakers will open？

（3）Point out the protective zone of Bus protection of 220kV Bus I in 220kV stimulation station.

4.5 Set 仿一线251 Disconnector 2511 A Phase porcelain flashover

（1）Fault phenomenon

| Equipment | Phenomenon |
| --- | --- |
| Master-control room： | 1．Fault Sound 2．Circuit breakers which are opening or closing： Bus voltage： 3．Message： 4．251仿一线monitoring detail drawing： |
| Protection room： Screen NO. |  |
| Protection room： Screen NO. |  |
| Protection room： Screen NO. |  |
| Protection room： Measurement and control screen |  |
| Protection room： 220kV line fault recording screen 110kV line fault fault recording screen Main transformer1 fault fault recording screen Main transformer2 fault fault recording screen |  |

（2）How to locate the fault according to the Fault phenomenon above?Why?

（3）After the fault,which equipments should the person on duty check seriously?Then work out the recovery process.

（4）How to isolate the failure equipments?

(5)  Which equipments(non-failure) are without power because of the fault?Then work out the recovery process.

4.6  Basic conception of Main transformer

（1）Which CT’s measured values do we need for protection device of Main transformer I in stimulation station?仿真（location of CT ）

（2）If protection device of Main transformer I in 220kV stimulation station operates，which Circuit breakers will open？

- Point out the protective zone of protection device of Main transformer I in 220kV stimulation station.

4.7 Restart ,then Set Main transformer I A phase bushing porcelain flashover

（1）Fault phenomenon

| Equipment | Phenomenon |
| --- | --- |
| Master-control room： | 1．Fault Sound 2．Circuit breakers which are opening or closing： Bus voltage： 3．Message： 4．251仿一线monitoring detail drawing： |
| Protection room： Screen NO. |  |
| Protection room： Screen NO. |  |
| Protection room： Screen NO. |  |
| Protection room： Measurement and control screen |  |
| Protection room： 220kV line fault recording screen 110kV line fault fault recording screen Main transformer1 fault fault recording screen Main transformer2 fault fault recording screen |  |

（2）How to locate the fault according to the Fault phenomenon above?Why?

（3）After the fault,which equipments should the person on duty check seriously?Then work out the recovery process.

- How to isolate the failure equipments?

(5)  Which equipments(non-failure) are without power because of the fault?Then work out the recovery process.